## 封页
版本号 | 修改日期 | 修改人 | 说明
V001 | 2024-03-21 | CLL | 初定版IBDC30060CAN协议及告警字

## IBDC30060CAN协议
Bidirectional DCDC Converter CAN Bus Protocol Data Sheet
Order | Data0 | Data1 | Data2 | Data Type | Fact | R/W
The following data is defined as DCDC unit data
0 | RSVD | RSVD | RSVD | USHORT | 1 | R
1 | RSVD | RSVD | RSVD | USHORT | 1 | R
2 | DCDC Fault area markings 0--No fault in the fault area 1--Fault area with fault set | System working status 0--Standby， 1--On Grid Running 2--Reserved 3--Off Grid Running 4--MPPT Running 5--Open loop Running 6--Debug Mode 7--Fault | Battery side working status 0--Standby 1--Charging 2--Discharging | USHORT | 1 | R
3 | Battery charging status 0--Standby 1--constant current 2--constant power 3--constant voltage 4--Floating charge 5--full charged | Charging power Unit：W | Discharging Power unit：W | SHORT | 1 | R
4 | Battery voltage Unit：V | Battery current Unit：A | RSVD | SHORT | 0.1 | R
5 | RSVD | RSVD | RSVD | SHORT | 0.1 | R
6 | RSVD | RSVD | RSVD | SHORT | 0.1 | R
7 | RSVD | RSVD | RSVD | SHORT | 0.1 | R
8 | BUS Voltage Unit：V | BUS+Voltage Unit：V | BUS-Voltage Unit：V | SHORT | 0.1 | R
9 | environmental temperature Unit：℃ | RSVD | RSVD | SHORT | 0.1 | R
10 | RSVD | RSVD | RSVD | USHORT | 1 | R
11 | RSVD | RSVD | DCDC Firmware version bit0 - bit6:debug version； bit7 - bit 10:beta version； bit11 - bit15:production version example：0x191D is：3.2.29 | USHORT | 1 | R
12 | DCDC software version bit0 - bit6:debug version； bit7 - bit 10:beta version； bit11 - bit15:production version example：0x191D is：3.2.29 | RSVD | RSVD | USHORT | 1 | R
13 | [1]DCDC warning word 0 | DCDC warning word 1 | DCDC warning word 2 | USHORT | 1 | R
14 | DCDC warning word 3 | DCDC warning word 4 | RSVD | USHORT | 1 | R
15 | RSVD | RSVD | RSVD | USHORT | 1 | R
16 | RSVD | RSVD | RSVD | USHORT | 1 | R
17 | RSVD | RSVD | RSVD | USHORT | 1 | R
18 | RSVD | RSVD | RSVD | USHORT | 1 | R
19 | RSVD | RSVD | RSVD | USHORT | 1 | R
20 | RSVD | RSVD | RSVD | USHORT | 1 | R
21 | RSVD | RSVD | RSVD | USHORT | 1 | R
22 | RSVD | RSVD | RSVD | USHORT | 1 | R
23 | RSVD | RSVD | RSVD | USHORT | 1 | R
24 | RSVD | RSVD | RSVD | USHORT | 1 | R
25 | RSVD | RSVD | RSVD | USHORT | 1 | R
26 | Can BUS Baud rate setting 0--1000kbps 1--500kbps 2--250kbps 3--125kbps Data Range[0,3] Default：3 | RSVD | RSVD | USHORT | 1 | R/W
27 | Certification Standard Code 0--Chinese standards I 1--Chinese standards II 2--American Standard 3--German Standard Data Range[0,3] Default：0 | RSVD | RSVD | USHORT | 1 | R/W
28 | RSVD | RSVD | RSVD | USHORT | 1 | R
29 | Fault clearing 0x0055--Clear all faults Default：0 | RSVD | RSVD | USHORT | 1 | R/W
30 | RSVD | RSVD | RSVD | USHORT | 1 | R
31 | Running status settings 0：adaptive 1：On Grid 2：Off Grid Data Range[0,2] Default：1 | RSVD | RSVD | USHORT | 1 | R/W
32 | System power on/off 0x0055 -- On 0x00AA -- Off Default：0x00AA | RSVD | RSVD | USHORT | 1 | R/W
33 | Restore factory settings 0x0055 -- Restore all values 0x00AA -- Restore user value Default：0 | RSVD | RSVD | USHORT | 1 | R/W
34 | Group ID Number Data Range[1,31] Default：1 | RSVD | RSVD | USHORT | 1 | R/W
35 | Module Number Data Range[1,31] Default：1 | RSVD | RSVD | USHORT | 1 | R/W
36 | RSVD | RSVD | RSVD | USHORT | 1 | R
37 | RSVD | RSVD | RSVD | USHORT | 1 | R
38 | RSVD | RSVD | RSVD | USHORT | 1 | R
39 | RSVD | RSVD | RSVD | USHORT | 1 | R
40 | RSVD | RSVD | RSVD | USHORT | 1 | R
41 | RSVD | RSVD | RSVD | USHORT | 1 | R
42 | RSVD | RSVD | RSVD | USHORT | 1 | R
43 | RSVD | RSVD | RSVD | USHORT | 1 | R
44 | RSVD | RSVD | RSVD | USHORT | 1 | R
45 | RSVD | RSVD | RSVD | USHORT | 1 | R
46 | RSVD | RSVD | RSVD | USHORT | 1 | R
47 | RSVD | RSVD | RSVD | USHORT | 1 | R
48 | Batteyr Type 0--Lead acid battery 1--lithium battery Data Range[0,1] Default：1 | RSVD | RSVD | USHORT | 1 | R/W
49 | RSVD | RSVD | RSVD | USHORT | 1 | R
50 | DC BUS Voltage Unit：V Data Range[6000,8500] Default：7200 | RSVD | RSVD | USHORT | 0.1 | R/W
51 | RSVD | RSVD | RSVD | USHORT | 1 | R
52 | Charge and discharge instructions 0--Standby 1--Charging 2--Dischargering 3--BAT Automatic switching 4--BUS Automatic switching 5--Turn off charging 6--High voltage PV mode Data Range[0,6] Default：1 | RSVD | RSVD | USHORT | 1 | R/W
53 | Charging and discharging power setting Unit：% Data Range[0,1300] Default：1000 | RSVD | RSVD | USHORT | 0.1 | R/W
54 | Battery balance charging voltage Unit：V Data Range[400,3600] Default：600 | RSVD | RSVD | USHORT | 0.1 | R/W
55 | Charging current setting Unit：A Data Range[0,1300] Default：1000 | RSVD | RSVD | USHORT | 0.1 | R/W
56 | Battery float charging voltage (not available for lithium batteries) Unit：V Data Range[400,3600] Default：600 | RSVD | RSVD | USHORT | 0.1 | R/W
57 | Discharge voltage setting Unit：V Data Range[400,3600] Default：400 | RSVD | RSVD | USHORT | 0.1 | R/W
58 | Discharge current setting Unit：A Data Range[0,1300] Default：1000 | RSVD | RSVD | USHORT | 0.1 | R/W
59 | Battery overvoltage shutdown Value Unit：V Data Range[400,3700] Default：3700 | RSVD | RSVD | USHORT | 0.1 | R/W
60 | Battery low voltage alarm value Unit：V Data Range[350,3550] Default：450 | RSVD | RSVD | USHORT | 0.1 | R/W
61 | Low voltage shutdown value of battery Unit：V Data Range[350,3550] Default：350 | RSVD | RSVD | USHORT | 0.1 | R/W
62 | Battery activation function 0--Disable 1--Enalbe Data Range[0,1] Default：0 | RSVD | RSVD | USHORT | 0.1 | R/W
63 | Automatic restart function 0--Disable 1--Enalbe Data Range[0,1] Default：0 | RSVD | RSVD | USHORT | 1 | R/W
64 | RSVD | RSVD | RSVD | USHORT | 1 | R
65 | RSVD | RSVD | RSVD | USHORT | 1 | R
66 | RSVD | RSVD | RSVD | USHORT | 1 | R
67 | RSVD | RSVD | RSVD | USHORT | 1 | R
68 | RSVD | RSVD | RSVD | USHORT | 1 | R
69 | RSVD | RSVD | RSVD | USHORT | 1 | R
70 | RSVD | RSVD | RSVD | USHORT | 1 | R
71 | RSVD | RSVD | RSVD | USHORT | 1 | R
72 | RSVD | RSVD | RSVD | USHORT | 1 | R
73 | RSVD | RSVD | RSVD | USHORT | 1 | R
74 | RSVD | RSVD | RSVD | USHORT | 1 | R
75 | RSVD | RSVD | RSVD | USHORT | 1 | R
76 | RSVD | RSVD | RSVD | USHORT | 1 | R
77 | RSVD | RSVD | RSVD | USHORT | 1 | R
78 | RSVD | RSVD | RSVD | USHORT | 1 | R
79 | RSVD | RSVD | RSVD | USHORT | 1 | R
80 | RSVD | RSVD | RSVD | USHORT | 1 | R
81 | RSVD | RSVD | RSVD | SHORT | 1 | R
82 | RSVD | RSVD | RSVD | USHORT | 1 | R
83 | RSVD | RSVD | RSVD | SHORT | 1 | R
84 | RSVD | RSVD | RSVD | USHORT | 1 | R
85 | RSVD | RSVD | RSVD | SHORT | 1 | R
86 | RSVD | RSVD | RSVD | USHORT | 1 | R
87 | RSVD | RSVD | RSVD | SHORT | 1 | R
88 | RSVD | RSVD | RSVD | USHORT | 1 | R
89 | RSVD | RSVD | RSVD | SHORT | 1 | R
90 | RSVD | RSVD | RSVD | USHORT | 1 | R
91 | RSVD | RSVD | RSVD | SHORT | 1 | R
92 | RSVD | RSVD | RSVD | USHORT | 1 | R
93 | RSVD | RSVD | RSVD | SHORT | 1 | R
94 | RSVD | RSVD | RSVD | USHORT | 1 | R
95 | RSVD | RSVD | RSVD | SHORT | 1 | R
96 | RSVD | RSVD | RSVD | USHORT | 1 | R
97 | RSVD | RSVD | RSVD | SHORT | 1 | R
98 | RSVD | RSVD | RSVD | USHORT | 1 | R
99 | RSVD | RSVD | RSVD | SHORT | 1 | R
100 | RSVD | RSVD | RSVD | USHORT | 1 | R
101 | RSVD | RSVD | RSVD | SHORT | 1 | R
102 | RSVD | RSVD | RSVD | USHORT | 1 | R
103 | RSVD | RSVD | RSVD | SHORT | 1 | R
104 | RSVD | RSVD | RSVD | USHORT | 1 | R
105 | RSVD | RSVD | RSVD | SHORT | 1 | R
106 | RSVD | RSVD | RSVD | USHORT | 1 | R
107 | RSVD | RSVD | RSVD | USHORT | 1 | R
108 | RSVD | RSVD | RSVD | USHORT | 1 | R
109 | RSVD | RSVD | RSVD | USHORT | 1 | R
110 | Alarm Mask code 1 Bit0--CAN communication enalbe Bit1--485 communication enalbe Data Range[0,32767] default：0 | RSVD | RSVD | USHORT | 1 | R/W
111 | RSVD | RSVD | RSVD | USHORT | 1 | R
112 | RSVD | RSVD | RSVD | USHORT | 1 | R
113 | RSVD | RSVD | RSVD | USHORT | 1 | R
114 | RSVD | RSVD | RSVD | USHORT | 1 | R
115 | RSVD | RSVD | RSVD | USHORT | 1 | R
116 | RSVD | RSVD | RSVD | USHORT | 1 | R
117 | RSVD | RSVD | RSVD | USHORT | 1 | R
118 | RSVD | RSVD | RSVD | USHORT | 1 | R
119 | RSVD | RSVD | RSVD | USHORT | 1 | R
120 | RSVD | RSVD | RSVD | USHORT | 1 | R
121 | RSVD | RSVD | RSVD | USHORT | 1 | R
122 | RSVD | RSVD | RSVD | USHORT | 1 | R
123 | RSVD | RSVD | RSVD | USHORT | 1 | R
124 | RSVD | RSVD | RSVD | USHORT | 1 | R
125 | RSVD | RSVD | RSVD | USHORT | 1 | R
注：USHORT（unsigned short ）为无符号短整型，SHORT（short） is a signed short integer ，实际值为数值*系数。

## IBDC30060告警字
告警字 | bit定义 | Fault Name | Remark
Warning word 0 | bit0 | Battery overvoltage alarm | 0：normal 1：occurs
| bit1 | Battery overvoltage shutdown | 0：normal 1：occurs
| bit2 | Battery fast overvoltage | 0：normal 1：occurs
| bit3 | Battery undervoltage alarm | 0：normal 1：occurs
| bit4 | Battery undervoltage shutdown | 0：normal 1：occurs
| bit5 | Battery fast undervoltage | 0：normal 1：occurs
| bit6 | Battery input short circuit | 0：normal 1：occurs
| bit7 | Charge discharge overcurrent | 0：normal 1：occurs
| bit8 | Fast overcurrent during charging and discharging | 0：normal 1：occurs
| bit9 | Charging and discharging hardware overcurrent | 0：normal 1：occurs
| bit10 | Battery not connected | 0：normal 1：occurs
| bit11 | Reverse battery connection | 0：normal 1：occurs
| bit12 | BUS3 overvoltage | 0：normal 1：occurs
| bit13 | BUS3 fast overvoltage | 0：normal 1：occurs
| bit14 | BUS3 undervoltage | 0：normal 1：occurs
| bit15 | BUS3 fast undervoltage | 0：normal 1：occurs
Warning word 1 | bit0 | BUS2 overvoltage | 0：normal 1：occurs
| bit1 | BUS2 fast overvoltage | 0：normal 1：occurs
| bit2 | 预留 | 0：normal 1：occurs
| bit3 | 预留 | 0：normal 1：occurs
| bit4 | 预留 | 0：normal 1：occurs
| bit5 | BUS2 undervoltage | 0：normal 1：occurs
| bit6 | 预留 | 0：normal 1：occurs
| bit7 | BUS1+overvoltage | 0：normal 1：occurs
| bit8 | BUS1+fast overvoltage | 0：normal 1：occurs
| bit9 | BUS1-overvoltage | 0：normal 1：occurs
| bit10 | BUS1-fast overvoltage | 0：normal 1：occurs
| bit11 | BUS1 Unbalanced voltage | 0：normal 1：occurs
| bit12 | BUS1+fast undervoltage | 0：normal 1：occurs
| bit13 | BUS1-fast undervoltage | 0：normal 1：occurs
| bit14 | BUS+overvoltage | 0：normal 1：occurs
| bit15 | BUS+ DC BUS fast overvoltage | 0：normal 1：occurs
Warning word 2 | bit0 | BUS-DC BUS overvoltage | 0：normal 1：occurs
| bit1 | BUS-DC BUS fast overvoltage | 0：normal 1：occurs
| bit2 | BUS voltage Unbalanced | 0：normal 1：occurs
| bit3 | DC BUS not connected | 0：normal 1：occurs
| bit4 | BUS Reverse connection | 0：normal 1：occurs
| bit5 | BUS short circuit | 0：normal 1：occurs
| bit6 | BUS undervoltage shutdown | 0：normal 1：occurs
| bit7 | BUS+fast undervoltage | 0：normal 1：occurs
| bit8 | BUS-fast undervoltage | 0：normal 1：occurs
| bit9 | DCDC1 over-current | 0：normal 1：occurs
| bit10 | DCDC1 fast over-current | 0：normal 1：occurs
| bit11 | DCDC1 Hardware overcurrent | 0：normal 1：occurs
| bit12 | DCDC2 overcurrent | 0：normal 1：occurs
| bit13 | DCDC2 fast overcurrent | 0：normal 1：occurs
| bit14 | DCDC2 Hardware overcurrent | 0：normal 1：occurs
| bit15 | DCDC3 overcurrent | 0：normal 1：occurs
Warning word 3 | bit0 | DCDC3 fast overcurrent | 0：normal 1：occurs
| bit1 | DCDC3 Hardware overcurrent | 0：normal 1：occurs
| bit2 | DCDC Unbalanced current | 0：normal 1：occurs
| bit3 | 预留1 | 0：normal 1：occurs
| bit4 | Resonant inductor A1 hardware overcurrent | 0：normal 1：occurs
| bit5 | 预留2 | 0：normal 1：occurs
| bit6 | Resonant inductor A2 hardware overcurrent | 0：normal 1：occurs
| bit7 | Overload 110% | 0：normal 1：occurs
| bit8 | Overload 125% | 0：normal 1：occurs
| bit9 | BuckBoost Soft start fault | 0：normal 1：occurs
| bit10 | DCDC BUS Soft start fault | 0：normal 1：occurs
| bit11 | DCDC Battery Soft start fault | 0：normal 1：occurs
| bit12 | BAT Overheating of radiator | 0：normal 1：occurs
| bit13 | DCDC Original side over-temperature | 0：normal 1：occurs
| bit14 | DCDC Sub-side over-temperature | 0：normal 1：occurs
| bit15 | DCDC environmental overheating | 0：normal 1：occurs
Warning word 4 | bit0 | Auxiliary power supply failure | 0：normal 1：occurs
| bit1 | DCDC power derating | 0：normal 1：occurs
| bit2 | DCDC Fan A Failure | 0：normal 1：occurs
| bit3 | DCDC Fan B Failure | 0：normal 1：occurs
| bit4 | E2PROM read faults | 0：normal 1：occurs
| bit5 | E2PROM write faults | 0：normal 1：occurs
| bit6 | DCDC Abnormal heartbeat detection | 0：normal 1：occurs
| bit7 | DCDC Software version error | 0：normal 1：occurs
| bit8 | Monitoring CAN BUS A communication failure | 0：normal 1：occurs
| bit9 | Parallel CAN BUS B communication failure | 0：normal 1：occurs
| bit10 | SPI Communication Failure | 0：normal 1：occurs
| bit11 | 485 Communication Failure | 0：normal 1：occurs
| bit12 | Main relay fault on the DC BUS side | 0：normal 1：occurs
| bit13 | Battery side main relay fault | 0：normal 1：occurs
| bit14 | DC Model configuration error | 0：normal 1：occurs
| bit15 | EPO Error | 0：normal 1：occurs